Please Note:

This template is intended for educational purposes only, without any express or implied warranty of any kind, including warranties of accuracy, completeness, or fitness for any particular purpose.  You agree that your use of the template is without any recourse whatsoever to PG&E, SCE, SDG&E, or their affiliates. The template is a draft, and anyone using this document should seek the advice of an attorney to develop appropriate ordinance language to meet its jurisdiction’s specific needs, as state and local laws may differ.

This document is the product of a collaborative effort between Peninsula Clean Energy, Silicon Valley Clean Energy, and the Local Energy Codes team.

Please contact the Codes and Standards Local Energy Codes Team at info@LocalEnergyCodes.com for additional information.

This program is funded by California utility customers and administered by Pacific Gas and Electric Company, San Diego Gas & Electric Company (SDG&E®), and Southern California Edison Company under the auspices of the California Public Utilities Commission and in support of the California Energy Commission.

REACH CODE IMPLEMENTATION RESOURCES TEMPLATE

2025 SINGLE FAMILY ELECTRIC READINESS CHECKLIST

Version 1.0, February 2026

This template is provided to assist local jurisdictions with the implementation of adopted reach codes. It is not intended to provide guidance on the development of a reach code ordinance. Anyone developing a reach code ordinance should seek the advice of an attorney to develop appropriate ordinance language to meet its jurisdiction’s specific needs, as state and local laws may differ. This template is intended for educational purposes only, without any express or implied warranty of any kind, including warranties of accuracy, completeness, or fitness for any particular purpose. You agree that your use of the template is without any recourse whatsoever to the developers of this document.

This document is intended as a compliance tool for typical 2025 local reach codes.  Modify it as needed to suit local requirements (especially blue italicized text).

# Scope

This checklist includes requirements for certain additions and alterations that align with the electric readiness model reach code.

# Instructions

- Make modifications following instructions and options in blue text. DELETE ALL BLUE TEXT BEFORE PUBLISHING

- Delete sections that do not apply, renumber sections as needed and edit requirements to align with local ordinance.

- Check all numbering and internal references after editing.

- Delete the cover page and this page.

This form is required for all electric readiness requirements for additions
and alterations to single family homes, duplexes and townhomes

These building standards have been established to ensure that construction in [jurisdiction] is healthier for occupants, has limited impact on the environment, reduces demand for energy, and results in cost savings from building operation over the life of the building. This checklist is intended to help applicants understand the process and specific local requirements that apply to their project.

For more information, please visit [jurisdiction website or other resource]

PROJECT PROCESS

- Project Design

It is important for project owners, architects, engineers, and designers to understand the applicable state and local building requirements prior to project design. Early consideration of these standards allows for design of buildings and systems that are compliant, energy efficient, and cost effective, and minimizes back and forth when applying for the project permit.

- Planning application (If required)

If your project is subject to planning review, be prepared to identify in your planning application which compliance methods you’ve selected and how you plan to meet the requirements. If you anticipate difficulties meeting the requirements, these concerns and any requests for exemptions should be identified in your planning application.

- Initial Building Permit Submittal

Include the following on your plans as part of your initial application for a building permit:

- Completed Local Building Decarbonization Checklist

- Title 24 Part 6 documentation demonstrating compliance with all State requirements

This form is required for all electric readiness requirements for additions and alterations to single family homes, duplexes and town homes

PROJECT ADDRESS:______________________________________________________________

APN:___________________ APPLICANT NAME:________________________________________

- Scope of Requirements.

Complete this form if the project scope includes any of the following activities in a single family home:

- Circuits are being added or altered within three feet of a gas water heater, range, stovetop, oven, or clothes dryer.

- Framing is being altered within 3 feet of a gas water heater.

- A gas line(s) is being extended to an outdoor appliance.

- Main electrical service panel is being upgraded.

These requirements are specified in Sections [specify local code sections].

2.  Electric Readiness

Check the boxes if the project includes the scope of work in the table.

Table 1: Electric Readiness

| Check | Scope | Requirement |
| --- | --- | --- |
|  | Water Heater: Circuit added or altered within 3 feet of an existing gas water heater or with 10’ of a designated location of a future water heater | Electric readiness* at 240V/30 amps |
|  | Water Heater: Wall framing removed or replaced adjacent to water heater | Reserve space for heat pump water heater (2.5 feet by 2.5 feet wide and 7 feet tall) and install a condensate drain |
|  | Range/Stovetop/Over: Kitchen circuit added or altered within 3 feet of a gas appliance | Electrical readiness* at 240V/50 amps |
|  | Clothes Dryer: Laundry area circuit added or altered within 3 feet of a gas appliance | Electrical readiness* at 240V/30 amps |
|  | Outdoor Gas Appliance: Gas line extended to outdoor appliance (other than an emergency power generator) | Install conduit or a circuit designed to serve a future electric appliance(s) with the same function, including the appropriate voltage, phase, minimum amperage, and an electrical receptacle or junction box within five feet of the appliance |

* Electric readiness: Within 3 feet of appliance install either a) a 120V/20 amp circuit, with conductors with capacity to support conversion to 3 conductor (plus ground) 240V circuit at the specified amperage or b) a raceway (conduit or sheathed cable) between main panel and an enclosure at the appliance capable of supporting a 3 conductor (plus ground) 240V circuit at the specified amperage.

3.  Electrical Service Panel Upgrade

This section must be completed for all projects involving an upgrade of the main electrical service panel.

Calculations are required in accordance with California Electrical Code Article 220.83 determining that future loads will exceed the capacity of the current electrical power infrastructure and calculations, and, where historical data are available, in accordance with California Electrical Code Article 220.87 determining that future loads exceed the capacity of the current electrical service infrastructure.

The calculations must include one of the following (check at least one):

- ☐	At least one power management or circuit controlling device, serving electric-only appliances such as: water heater; clothes dryer; range; Level 2 EV charging receptacle; or Low Power Level 2 EV charging receptacle.

Specify the appliance: __________________

- ☐	At least one of the following electric-only appliances operating on 120V: water heater; clothes dryer; range.

Specify the appliance: __________________

- ☐	Circuit control between whole home load and Level 2 EV Charging Receptacle or Low Power Level 2 EV Charging Receptacle

Calculations are provided as part of the plan submittals:

California Electrical Code Article 220.83

California Electrical Code Article 220.87

Data are not available to support Article 220.87 calculations

State reason: ____________________________________________

Exemption

The panel upgrade is for required electrical improvements supporting loads other than water heaters, dryers, ranges/stovetops/ovens, or electric vehicle chargers.

Specify end use that requires panel upgrade: __________________

4.	Project Verification

This form has been completed by _________________(name) of ________________(company), the qualified [specify credentials based on local practice, e.g., architect, engineer, project manager] individual for the above listed project who verifies that it accurately represents the project plans. [modify based on local verification requirements]

________________________________			______________

Signature								Date