Please Note:

This template is intended for educational purposes only, without any express or implied warranty of any kind, including warranties of accuracy, completeness, or fitness for any particular purpose. You agree that your use of the template is without any recourse whatsoever to PG&E, SCE, SDG&E, or their affiliates. The template is a draft, and anyone using this document should seek the advice of an attorney to develop appropriate ordinance language to meet its jurisdiction’s specific needs, as state and local laws may differ.

This document is the product of a collaborative effort between Peninsula Clean Energy, Silicon Valley Clean Energy, and the Local Energy Codes team.

Please contact the Codes and Standards Local Energy Codes Team at info@LocalEnergyCodes.com for additional information.

This program is funded by California utility customers and administered by Pacific Gas and Electric Company, San Diego Gas & Electric Company (SDG&E®), and Southern California Edison Company under the auspices of the California Public Utilities Commission and in support of the California Energy Commission.

REACH CODE IMPLEMENTATION RESOURCES TEMPLATE

2025 SINGLE FAMILY AIR CONDITIONER ADDITION
 or REPLACEMENT CHECKLIST

Version 1.0, February 2026

This template is provided to assist local jurisdictions with the implementation of adopted reach codes. It is not intended to provide guidance on the development of a reach code ordinance. Anyone developing a reach code ordinance should seek the advice of an attorney to develop appropriate ordinance language to meet its jurisdiction’s specific needs, as state and local laws may differ. This template is intended for educational purposes only, without any express or implied warranty of any kind, including warranties of accuracy, completeness, or fitness for any particular purpose. You agree that your use of the template is without any recourse whatsoever to the developers of this document.

This document is intended as a compliance tool for typical 2025 local reach codes.  Modify it as needed to suit local requirements (especially blue italicized text).

# Scope

This checklist includes requirements for additions and replacements of central air conditioners in existing single family homes, duplexes, and townhomes.

# Instructions

- Make modifications following instructions and options in blue text. DELETE ALL BLUE TEXT BEFORE PUBLISHING

- Delete sections that do not apply, renumber sections as needed and edit requirements to align with local ordinance.

- Check all numbering and internal references after editing.

- Delete the cover page and this page.

This form is required for all air conditioner additions and replacements
 in single family homes, duplexes, and townhomes

These building standards have been established to ensure that construction in [jurisdiction] is healthier for occupants, has limited impact on the environment, reduces demand for energy, and results in cost savings from building operation over the life of the building. This checklist is intended to help applicants understand the process and specific local requirements that apply to their project.

For more information, please visit [jurisdiction website or other resource]

PROJECT PROCESS

- Project Design

It is important for project owners, architects, engineers, and designers to understand the applicable state and local building requirements prior to project design. Early consideration of these standards allows for design of buildings and systems that are compliant, energy efficient, and cost effective, and minimizes back and forth when applying for the project permit.

- Planning application (If required)

If your project is subject to planning review, be prepared to identify in your planning application which compliance methods you’ve selected and how you plan to meet the requirements. If you anticipate difficulties meeting the requirements, these concerns and any requests for exemptions should be identified in your planning application.

- Initial Building Permit Submittal

Include the following on your plans as part of your initial application for a building permit:

- Completed Local Building Decarbonization Checklist

- Title 24 Part 6 documentation demonstrating compliance with all State requirements

This form is required for all air conditioner additions and replacements 
in single family homes, duplexes, and town homes

PROJECT ADDRESS:______________________________________________________________

APN:___________________ APPLICANT NAME:________________________________________

- Scope of Requirements

Complete this form if the project scope includes replacing an existing or adding a new central air conditioner in a single family home, duplex, or townhome.

These requirements are specified in Sections [specify local code sections].

2.	Air Conditioner Addition or Replacement

Complete section A, B, C or D below for all projects involving the addition or replacement of a central air conditioner (other than a portable unit). All Section references refer to the standards of the California Energy Code.

- Air Conditioner with Heat Pump

The replacement includes a heat pump that meets the requirements of the California Energy Code Sections 110.2, 150.0(h)7, and either 150.2(b)1.C, or 150.2(b)1.E, 150.2(b)1.F, and 150.2(b)1.G, as applicable, and locks out supplementary heating (if applicable) above an outdoor air temperature of no greater than 35°F.

B.	Air Conditioner without Heat Pump. Complete Section i or ii.

i.	New Ducts (check all items below)

The replacement air conditioning system meets the requirements of Sections 110.2, 150.0(h)7, 150.2(b)1.C, 150.2(b)1.E, 150.2(b)1.F, and 150.2(b)1.G

Meet all additional local requirements:

Achieve fan efficacy of 0.35 w/cfm or less based on Section150.0(m)13B, 150.0(m)13C, or 150.0(m)13D.

Verify refrigerant charge based on Section 150.2(b)Fii

Insulate ducts in unconditioned space to R-8

ii.	Existing Ducts (check all items below)

Meet the requirements of Sections 110.2, 150.0(h)7, 150.2(b)1D, 150.2(b)1E, 150.2(b)1F i-iii, and 150.2(b)1G

Meet all additional local requirements:

Achieve fan efficacy of 0.45 w/cfm based on Section150.0(m)13B-D

Verify refrigerant charge based on Section 150.2(b)1Fii

Install attic insulation to achieve a U-factor of 0.020 or insulation installed at the ceiling level shall result in an insulated thermal resistance of R-49 or greater for the insulation alone (check this box or at least one of the exceptions below).

Exceptions to attic insulation requirement:

    - Existing R-38 insulation

    - Attic with asbestos or knob and tube wiring

    - Accessible space is filled, but does not fit R-49 insulation

    - Shared attic with another dwelling unit without firewall

Air seal all accessible areas of the ceiling plane between the attic and the conditioned space in accordance with Section 110.7 (check this box or at least one of the exceptions below).

Exceptions to air sealing requirement:

Existing R-38 insulation

Attic with asbestos

A gas space heater or water heater is located inside the dwelling unit

C. Performance Approach

Demonstrate compliance with the performance approach of California Energy Code Section 150.2(b)2, as locally amended. Attach supporting documentation.

D. Exceptions to Local Requirements (all California Energy Code requirements still apply)

Where the capacity of the existing main electrical service panel is insufficient to supply the electrical capacity of a heat pump and where the existing main electrical service panel is sufficient to supply a new or replacement air conditioner, as calculated according to the requirements of California Electrical Code Article 220.83 or Article 220.87, systems shall comply with the applicable requirements of Sections 150.2(b)1Fi, 150.2(b)1Fii, and 150.2(b)1Fiii. Documentation of electrical load calculations in accordance with Article 220 must be submitted to the enforcement agency prior to permitting for both the heat pump and proposed air conditioner.

Where the required capacity of a heat pump to meet the system selection requirements of Section 150.0(h)5 is greater than or equal to 12,000 Btu/h more than the greater of the required capacity of an air conditioner to meet the design cooling load OR the capacity of the existing air conditioner, systems shall comply with the applicable requirements of Sections 150.2(b)1Fi, 150.2(b)1Fii, and 150.2(b)1Fiii. Documentation of heating and cooling load calculations in accordance with 150.0(h) must be submitted to the enforcement agency prior to permitting for both the heat pump and proposed air conditioner.

- Project Verification

This form has been completed by _________________(name) of ________________(company), the qualified [specify credentials based on local practice, e.g., architect, engineer, project manager] individual for the above listed project who verifies that it accurately represents the project plans. [modify based on local verification requirements]

________________________________			______________

Signature								Date